## 91502
Method for Determining if a Direct Branch Connection Will Meet a Design Condition Without Reinforcement
And if it Does Not, the Extent of Reinforcement Needed
Instructions:
(1) Enter the required branch angle in cell B26. Set cell J25 to zero.
(2) Enter the pipe data in cells A31 to H31. For welded pipe, if the weld seam of the main is not cut use S without the E factor.
(3) If the design pressure is higher than the joint pressure, JP, pressure, reinforcement is required.
(4) To calculate reinforcement area enter the pipe data on line 41 with your design pressure under P.
(5) The required sq in of reinforcement will be under A4. Enter this number in cell J25.
(6) The JP col on line 31 will then show your design pressure and the area check.
Sample Material Allowable Stresses:
[6 empty] | A106B,A53B Smls |  | S = | 17100 | psi
JP = | Allowable joint pressure |  |  |  |  | A53B,ERW |  | SE= | 14600
= | 2ShSb(dbTh+Tb^2(5+sin a)) |  |  |  |  | Same, Seam Uncut |  | S = | 17100
| (SbdbDh(3-sin a)+5ShTbDb) |  |  |  |  | A53F, BW, Cont.Weld |  | SE = | 8200
[6 empty] | Same, Seam Uncut |  | S = | 14600
JP = | Allowable joint pressure
P= | 2St/D |  |  |  |  | A7 = | th x d1 x (2-sina) ,sq.in.,(sq.mm.)
D = | Nominal pipe OD |  |  |  |  | A1 = | (2d2-d1)(Th-th)= db/sin a(Tm-PDm/2Sm), sq in(sq mm)
t = | Required pipe wall = |  | PD/2S |  |  | A2 = | 5Tb/sin a(Tb-tb), sq in (sq mm)
T = | T-A, Nominal pipe wall less tolerance & corrosion. |  |  |  |  | A3 = | 2(0.7Tb)^2, sq in (sq mm)
h = | main, header |  |  |  |  | A4 = | reinforcement, if needed, sq in (sq mm)
b = | branch |  |  |  |  | db = | Db-2Tb
[6 empty] | d1 = d2 = | db/sina
Br.angle | deg | rad |  |  |  |  | A4 = | sq in | 0
a = | 90 | 1.5708 | sin a = | 1 |  |  |  | sq mm | 0
Main |  |  |  | Branch | [5 empty] | Max Main | Max Br
Size | Sh | Dh | Th | Size | Sb | Db | Tb |  | JP | Pm | Pb
in | psi | in | in | in | psi | in | in |  | psi
24 | 14600 | 24 | 0.297 | 12 | 14600 | 12.75 | 0.297 |  | 200.65 | 361.35 | 680.1882
Area Check:
A7 | S A1 to A4 | A1 | A2 | A3 | A4 |  | db
sq in | sq in | sq in | sq in | sq in | sq in |  | in
2.0047 | 2.003 | 1.6056 | 0.31094 | 0.086445 | 0 |  | 12.156
Reinforcement:
Main |  |  |  | Branch
Size | Sh | Dh | Th | Size | Sb | Db | Tb | P | A4 Reinf. | db
in | psi | in | in | in | psi | in | in | psi | sq in
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
Metric
Size | Sh | Dh | Th | Size | Sb | Db | Tb |  | PF | Pm | Pb
DN | kPa | mm | mm | DN | k/Pa | mm | mm |  | kPa | k/Pa | k/Pa
200 | 103425 | 219.1 | 8.18 | 100 | 88256 | 114.3 | 6.02 |  | 4463.4714 | 7722.6518 | 9296.6075
25 | 6.895 | 25.4 | 25.4 | 25 | 6.895 | 25.4 | 25.4 |  | 6.895 | 6.895 | 6.895
8 | 15000 | 8.626 | 0.32205 | 4 | 12800 | 4.5 | 0.23701 |  | 647.349 | 1120.0365 | 1348.3115
Area Check:
A7 | S A1 to A4 | A1 | A2 | A3 | A4 |  | db
sq mm | sq mm | sq mm | sq mm | sq mm |  |  | mm
483.4654 | 482.7406 | 353.0214 | 94.2036 | 35.5156 | 0 |  | 102.26